## Notes
UPS Fleet Monitor | Operating Summary · Simulated Data
Historical Boundary | State immediately before the cutoff; later acknowledgments/recoveries are excluded
Source | Simulated Data / simulation
Session | session-1
Generation | g3
Seed | 7
Current Scenario Version | missing/1.0; historical rows identify their source scenario
Template / Dictionary | REP-01 / 1.0
Start (Inclusive) | 2026-09-13 08:00
End (Exclusive) | 2026-09-14 08:00
Time Zone | Asia/Singapore
Data Cutoff | 2026-09-14 08:00
Generated At | 2026-09-14T16:52:01.662Z
Statistical Method | Valid-time weighting; gaps are not filled with zero; source peaks; simulated assessments are not certified
Completeness | Full coverage for the selected metrics

## Metric Dictionary
ID | Name | Definition | Unit | Location | Basis | Formula | Threshold
KPI-01 | Power Mode | The equipment's operating mode, independent of communication status. | Status | UPS | Vendor Protocol Enumeration | Not Calculated | No universal numeric threshold; display the mapped state.
KPI-02 | Equipment Identity | Name, model, location, and selected asset identity. This is not a performance score. | — | Asset Register | Vendor Model and Engineering Asset Register | Not Calculated | No Performance Threshold
KPI-03 | Estimated Runtime R | Remaining supply time estimated by the equipment at the current load. This is not a guaranteed duration. | min | UPS | Equipment Runtime Algorithm | Estimated by the equipment; not inferred linearly from voltage. | Triggered when R < Q. Q is a project requirement, not a universal industry limit.
KPI-04 | Required Runtime Q and Margin | Q comes from project business requirements. Margin is estimated runtime minus required runtime. | min | UPS / Project Requirement | Project Continuity Requirement | M = R − Q, calculated only when R is valid. | Q, recovery hysteresis, and valid-sample gates follow the approved configuration.
KPI-05 | Overall Health Score | An independent vendor or approved external assessment. Do not combine SOC, SOH, or alarm counts into a score. | 0–100 points | UPS | Approved External Overall Health Method | This project defines no universal overall health formula. | Without a valid score, show a neutral unassessed ring. A high score does not override critical risk.
KPI-06 | Battery Asset | Chemistry, cell count, and identity of the selected battery string. | cells | Selected Battery String | Vendor Battery Register | Not Calculated | Different battery chemistries must not share an assumed default threshold.
KPI-07 | Battery String Voltage | Voltage across the selected string terminals, distinct from individual cell voltage. | V | Battery String Terminals | Model Point List, Scaling, and Measurement Location | Raw value × approved scale + offset | Vendor operating limits are pending; no universal limit is assumed.
KPI-08 | Impedance and Baseline | A result from a specified measurement method. DC resistance and AC impedance are not interchangeable. | mΩ / % | Selected Battery String | Baseline Using the Same Instrument, Method, Temperature, and Charge State | Change = (current − baseline) / baseline × 100%; baseline > 0 | R-03 requires vendor thresholds or an approved baseline.
KPI-09 | Battery Temperature | Temperature at the battery sensor location. | °C / °F | Selected Battery String | Vendor Temperature Sensor Definition | °F=°C×1.8+32 | Vendor temperature limits are pending. No cross-chemistry default is used.
KPI-10 | Charge / Discharge Current | Charging or bidirectional battery current with its sign convention preserved. | A | Battery String Circuit | Measurement Direction in the Point List | Normalize raw current; a negative sign alone does not indicate a fault. | The sign convention follows the source point mapping.
KPI-11 | SOC and SOH | SOC indicates remaining charge. SOH is capacity-based or vendor-defined health; they are independent. | % | Selected Battery String | Vendor Capacity-Based SOH Definition | Capacity SOH = measured capacity / reference rated capacity × 100% under matching conditions. SOC uses the vendor full-charge reference. | No universal retirement threshold across chemistries.
KPI-12 | Battery History | Explicit SOC or SOH history with a time axis, units, and quality gaps. | % | Selected Battery String | FIN History | Aggregate valid samples; do not fill gaps with zero or connect lines across gaps. | Do not extrapolate service life from the curve.
KPI-13 | Battery Maintenance / Replacement Window | A date range from a maintenance plan, vendor recommendation, or traceable external prediction. | Date Range | Battery Component | Maintenance Plan or External Model | Do not calculate unverified remaining months. | If the source, method, or valid dates are incomplete, show Not Assessed.
KPI-14 | Active / Apparent Power and Ratings | Compare kW and kVA with their respective ratings on the same basis. Do not divide one by the other for load percentage. | kW / kVA | UPS Output / Nameplate | Model Ratings and Derating Conditions | Power is measured; ratings are asset configuration values. | Rated capacity is stored per equipment item.
KPI-15 | Load Percentage | Power as a percentage of rated capacity on the same basis. Use a distinct name for a different native definition. | % | UPS Output | Vendor Load Definition and Project Rules | P / rated P × 100% or S / rated S × 100%; use the declared mapping basis. | Thresholds, hysteresis, and gates follow approved project rules. Preserve values above 100%.
KPI-16 | Load History | Time series using the declared load basis. | % | UPS | Source Sample History | Weighted by Valid Time | Do not fill gaps with zero. Report coverage and source peaks separately.
KPI-17 | Output Voltage and Frequency | Identify the output or internal inverter location, phase, and line-to-line or phase voltage basis. | V / Hz | L1-N / UPS Output | Vendor Performance Declaration; IEC 62040-3 Provides Background Only | Direct Measurement | Specific tolerances await equipment and project design. No standards conformity is certified.
KPI-18 | Output THD | Distinguish THDv from THDi and THD-F from THD-R. | % | Output L1 / Voltage | Vendor THD-F Measurement Window | THD-F=√Σ(Xn²,n≥2)/X1×100% | Slow history cannot reconstruct harmonics. Vendor limits must be registered.
KPI-19 | Rectifier / Charger | Rectifier operation and charging operation are separate states. | Status | Power Module | Vendor Enums and Operating States | Not Calculated | Unknown must not be displayed as Normal.
KPI-20 | Cooling Fan | Actual fan feedback, not a remaining-life percentage. | Status | Selected Power Module | Vendor Fan Diagnostic Enumeration | Not Calculated | Do not display remaining life without evidence.
KPI-21 | Capacitor Health | A vendor or external assessment percentage, not a universal direct measurement. | % | Capacitor Bank | Vendor Capacitor Assessment Method | Use a traceable external assessment, not an invented algorithm. | Without a source, leave the track empty. Do not fill it to 100%.
KPI-22 | Ambient Temperature | Room or cabinet sensor temperature, distinct from battery temperature. | °C / °F | Associated Space / Environmental Sensor | Sensor Location and Vendor Operating Conditions | °F=°C×1.8+32 | 20–25°C is not an automatically enforced project standard.
KPI-23 | Relative Humidity | Relative humidity in the specified space. Retain out-of-range observations but exclude them from assessment. | %RH | Associated Space | Vendor Sensor Range | Not Calculated | Out-of-range observations are not valid inputs.
KPI-24 | Air Quality | Specify the pollutant, unit, or defined classification system. | μg/m³ / Class | Associated Space Sensor | PM2.5 and Vendor Classification | Use the Sensor Definition | Do not label an arbitrary index as a standardized AQI.
KPI-25 | Water Detection | Three states: Dry, Water Detected, and Unknown. | Boolean / State | Leak Sensor Area | Vendor Digital Input Enumeration | false = Dry; true = Water Detected; null = Unknown | Unknown does not mean Dry.
KPI-26 | Transfer Status | Actual equipment transfer-switch state. | Status | UPS Transfer Switch | Vendor Switch Enumeration | Not Calculated | Do not infer power mode from communication status.
KPI-27 | Static / Maintenance Bypass | Availability and activation represent capability and present engagement separately. | Boolean / State | Static Bypass / Maintenance Bypass | Vendor UPS and Switch Enums | Independent fields; do not infer one from another. | Available does not mean Active. Keep the state Unknown when disconnected.
KPI-28 | Last Transfer Duration | Transfer duration recorded by the equipment. | ms | Equipment Transfer Event | Trusted Equipment Event | Use measured event duration, not a polling interval. | Without event evidence, show Unsupported.
KPI-29 | Last Transfer Time | The timestamp of the last equipment transfer event, including its time zone. | ISO Timestamp | Equipment Event | Native event record | Not Calculated | Not the page refresh or receipt time
KPI-30 | Maintenance Outlook | Manual plans or external recommendations for batteries, capacitors, and fans. | Date Range | Applicable component | Plan owner, manufacturer recommendation, or existing model | No proprietary prediction is generated | No month estimate without a source; manual plans are clearly identified
KPI-31 | Alarms & Events | FIN occurrence, recovery, and acknowledgment are independent lifecycle events. | Event / Time | Current UPS alarm scope | Native instance and lifecycle | New occurrences and carry-over instances are counted separately | Ordinary events are excluded from alarm counts
KPI-32 | Active / Unacknowledged Count | Active instances and unacknowledged instances in the current scope are counted separately. | items | Current filters and authorized scope | FIN native lifecycle | Deduplicate by instance ID; acknowledgment does not change active state | Acknowledged critical alarms remain critical; counts are unknown when the source is unavailable

## Data Quality
Equipment | Metric | Valid Samples | Total Samples | Coverage % | Valid Mean | Source Minimum | Source Maximum
UPS-01 | loadPct | 288 | 288 | 100 | 43.918 | 38 | 49.8
UPS-01 | runtimeEstimateMinutes | 288 | 288 | 100 | 31.976 | 30 | 34
UPS-01 | batterySoc | 288 | 288 | 100 | 96.987 | 96 | 98
UPS-01 | batterySoh | 288 | 288 | 100 | 93.998 | 93.8 | 94.2
UPS-02 | loadPct | 288 | 288 | 100 | 50.89 | 45.2 | 56.9
UPS-02 | runtimeEstimateMinutes | 288 | 288 | 100 | 28.984 | 27 | 31
UPS-02 | batterySoc | 288 | 288 | 100 | 96.991 | 96 | 98
UPS-02 | batterySoh | 288 | 288 | 100 | 91.997 | 91.8 | 92.2

## Current Health
Equipment | SOC% | SOH% | Simulated Health Score | Risk | Coverage | Assessed At | Basis | Source | Active Alarms | Unacknowledged
UPS-01 |  |  |  | attention | partial | 2026-09-14 08:03 | sim-assessment-v1 | Simulated Data | 2 | 1
UPS-02 |  |  |  | attention | partial | 2026-09-14 08:03 | sim-assessment-v1 | Simulated Data | 1 | 1

## Operating Summary
Equipment | Model | Average Load % | Source Peak % | Minimum Runtime min | Load Coverage % | Valid Mode at Cutoff | Valid Source Time
UPS-01 | SIM Online 60kW | 43.92 | 49.8 | 30 | 100 | utility | 2026-09-14 07:55
UPS-02 | SIM Online 80kW | 50.89 | 56.9 | 27 | 100 | utility | 2026-09-14 07:55

## Details
Equipment | Source Time (Selected Time Zone) | Metric | Value | Unit | Quality | Coverage % (Bucket) | Mapping Version | Source | Scenario Version | Source Reference
UPS-01 | 2026-09-13 08:00 | loadPct | 43.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:05 | loadPct | 40.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:10 | loadPct | 40.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:15 | loadPct | 39.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:20 | loadPct | 40.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:25 | loadPct | 42.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:30 | loadPct | 46.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:35 | loadPct | 48.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:40 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:45 | loadPct | 49.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:50 | loadPct | 45.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:55 | loadPct | 43.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:00 | loadPct | 41.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:05 | loadPct | 39.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:10 | loadPct | 39.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:15 | loadPct | 39.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:20 | loadPct | 43.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:25 | loadPct | 45.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:30 | loadPct | 46.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:35 | loadPct | 49.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:40 | loadPct | 48 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:45 | loadPct | 47.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:50 | loadPct | 43.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 09:55 | loadPct | 41.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:00 | loadPct | 40.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:05 | loadPct | 39 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:10 | loadPct | 40.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:15 | loadPct | 41.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:20 | loadPct | 44.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:25 | loadPct | 47.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:30 | loadPct | 48.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:35 | loadPct | 48.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:40 | loadPct | 48.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:45 | loadPct | 44.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:50 | loadPct | 42.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 10:55 | loadPct | 40.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:00 | loadPct | 38.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:05 | loadPct | 39.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:10 | loadPct | 41.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:15 | loadPct | 43.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:20 | loadPct | 46.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:25 | loadPct | 47.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:30 | loadPct | 48.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:35 | loadPct | 48.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:40 | loadPct | 46.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:45 | loadPct | 44.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:50 | loadPct | 41.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 11:55 | loadPct | 39.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:00 | loadPct | 38.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:05 | loadPct | 40.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:10 | loadPct | 43.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:15 | loadPct | 45.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:20 | loadPct | 46.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:25 | loadPct | 49.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:30 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:35 | loadPct | 46.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:40 | loadPct | 43.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:45 | loadPct | 42.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:50 | loadPct | 39.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 12:55 | loadPct | 39.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:00 | loadPct | 39.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:05 | loadPct | 41 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:10 | loadPct | 44.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:15 | loadPct | 48 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:20 | loadPct | 47.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:25 | loadPct | 48.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:30 | loadPct | 47.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:35 | loadPct | 45.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:40 | loadPct | 42 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:45 | loadPct | 40.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:50 | loadPct | 39.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 13:55 | loadPct | 39.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:00 | loadPct | 40.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:05 | loadPct | 43.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:10 | loadPct | 45.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:15 | loadPct | 47.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:20 | loadPct | 48.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:25 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:30 | loadPct | 46.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:35 | loadPct | 43.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:40 | loadPct | 40 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:45 | loadPct | 39.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:50 | loadPct | 40 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 14:55 | loadPct | 41.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:00 | loadPct | 42.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:05 | loadPct | 46.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:10 | loadPct | 47.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:15 | loadPct | 48.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:20 | loadPct | 49.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:25 | loadPct | 47.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:30 | loadPct | 43.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:35 | loadPct | 42.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:40 | loadPct | 39 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:45 | loadPct | 38 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:50 | loadPct | 39.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 15:55 | loadPct | 41.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:00 | loadPct | 44.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:05 | loadPct | 47.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:10 | loadPct | 48.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:15 | loadPct | 48.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:20 | loadPct | 46.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:25 | loadPct | 45.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:30 | loadPct | 42.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:35 | loadPct | 40.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:40 | loadPct | 38.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:45 | loadPct | 39.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:50 | loadPct | 41 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 16:55 | loadPct | 43.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:00 | loadPct | 45.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:05 | loadPct | 48.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:10 | loadPct | 48.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:15 | loadPct | 48 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:20 | loadPct | 45.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:25 | loadPct | 42.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:30 | loadPct | 41.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:35 | loadPct | 38.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:40 | loadPct | 39.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:45 | loadPct | 41.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:50 | loadPct | 42.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 17:55 | loadPct | 46.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:00 | loadPct | 47.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:05 | loadPct | 49.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:10 | loadPct | 47.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:15 | loadPct | 47.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:20 | loadPct | 44.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:25 | loadPct | 40.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:30 | loadPct | 38.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:35 | loadPct | 38.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:40 | loadPct | 39.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:45 | loadPct | 41.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:50 | loadPct | 45.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 18:55 | loadPct | 47.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:00 | loadPct | 49.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:05 | loadPct | 49.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:10 | loadPct | 47.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:15 | loadPct | 44.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:20 | loadPct | 42.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:25 | loadPct | 40.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:30 | loadPct | 38.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:35 | loadPct | 38.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:40 | loadPct | 40.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:45 | loadPct | 44.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:50 | loadPct | 47.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 19:55 | loadPct | 49.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:00 | loadPct | 48 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:05 | loadPct | 48.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:10 | loadPct | 45.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:15 | loadPct | 42.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:20 | loadPct | 40 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:25 | loadPct | 39.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:30 | loadPct | 39.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:35 | loadPct | 40.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:40 | loadPct | 42.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:45 | loadPct | 45.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:50 | loadPct | 49.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 20:55 | loadPct | 48.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:00 | loadPct | 47.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:05 | loadPct | 45.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:10 | loadPct | 43 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:15 | loadPct | 42 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:20 | loadPct | 38.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:25 | loadPct | 38.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:30 | loadPct | 41 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:35 | loadPct | 41.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:40 | loadPct | 45.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:45 | loadPct | 47.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:50 | loadPct | 48.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 21:55 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:00 | loadPct | 47.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:05 | loadPct | 44.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:10 | loadPct | 42.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:15 | loadPct | 40.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:20 | loadPct | 39.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:25 | loadPct | 39.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:30 | loadPct | 42.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:35 | loadPct | 44 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:40 | loadPct | 46.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:45 | loadPct | 49.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:50 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 22:55 | loadPct | 47.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:00 | loadPct | 45.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:05 | loadPct | 42.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:10 | loadPct | 41 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:15 | loadPct | 38.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:20 | loadPct | 38.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:25 | loadPct | 41.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:30 | loadPct | 43.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:35 | loadPct | 45.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:40 | loadPct | 47.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:45 | loadPct | 49.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:50 | loadPct | 48.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 23:55 | loadPct | 46.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 | loadPct | 44.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 00:05 | loadPct | 40.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 00:10 | loadPct | 39.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 00:15 | loadPct | 38.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 00:20 | loadPct | 40.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 00:25 | loadPct | 42.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 00:30 | loadPct | 46.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 00:35 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 00:40 | loadPct | 49.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 00:45 | loadPct | 49.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 00:50 | loadPct | 46.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 00:55 | loadPct | 45.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:00 | loadPct | 41.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:05 | loadPct | 39.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:10 | loadPct | 39.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:15 | loadPct | 40.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:20 | loadPct | 42.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:25 | loadPct | 44.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:30 | loadPct | 47.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:35 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:40 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:45 | loadPct | 48.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:50 | loadPct | 45.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 01:55 | loadPct | 42.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:00 | loadPct | 41 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:05 | loadPct | 38.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:10 | loadPct | 39.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:15 | loadPct | 41 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:20 | loadPct | 43.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:25 | loadPct | 45.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:30 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:35 | loadPct | 49.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:40 | loadPct | 48 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:45 | loadPct | 45.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:50 | loadPct | 43.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 02:55 | loadPct | 40.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:00 | loadPct | 38.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:05 | loadPct | 38.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:10 | loadPct | 39.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:15 | loadPct | 43.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:20 | loadPct | 46.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:25 | loadPct | 48.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:30 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:35 | loadPct | 48.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:40 | loadPct | 46.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:45 | loadPct | 43.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:50 | loadPct | 42.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 03:55 | loadPct | 39.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:00 | loadPct | 38.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:05 | loadPct | 40.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:10 | loadPct | 42.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:15 | loadPct | 44.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:20 | loadPct | 46.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:25 | loadPct | 49.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:30 | loadPct | 48.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:35 | loadPct | 48.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:40 | loadPct | 44.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:45 | loadPct | 43.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:50 | loadPct | 40.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 04:55 | loadPct | 39.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:00 | loadPct | 39.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:05 | loadPct | 41.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:10 | loadPct | 43.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:15 | loadPct | 47.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:20 | loadPct | 47.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:25 | loadPct | 49.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:30 | loadPct | 47.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:35 | loadPct | 45.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:40 | loadPct | 42.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:45 | loadPct | 40.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:50 | loadPct | 39.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 05:55 | loadPct | 40 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:00 | loadPct | 40 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:05 | loadPct | 42.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:10 | loadPct | 46.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:15 | loadPct | 47.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:20 | loadPct | 48.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:25 | loadPct | 48.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:30 | loadPct | 46.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:35 | loadPct | 43.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:40 | loadPct | 41.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:45 | loadPct | 40.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:50 | loadPct | 39.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 06:55 | loadPct | 40.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:00 | loadPct | 43 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:05 | loadPct | 45 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:10 | loadPct | 47.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:15 | loadPct | 49.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:20 | loadPct | 49.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:25 | loadPct | 48 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:30 | loadPct | 44.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:35 | loadPct | 42.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:40 | loadPct | 40.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:45 | loadPct | 39.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:50 | loadPct | 40.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-14 07:55 | loadPct | 41.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:loadPct
UPS-01 | 2026-09-13 08:00 | runtimeEstimateMinutes | 31.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:05 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:10 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:15 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:20 | runtimeEstimateMinutes | 30.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:25 | runtimeEstimateMinutes | 31.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:30 | runtimeEstimateMinutes | 32.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:35 | runtimeEstimateMinutes | 33.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:40 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:45 | runtimeEstimateMinutes | 33.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:50 | runtimeEstimateMinutes | 33 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:55 | runtimeEstimateMinutes | 31.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:00 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:05 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:10 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:15 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:20 | runtimeEstimateMinutes | 31.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:25 | runtimeEstimateMinutes | 32.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:30 | runtimeEstimateMinutes | 33.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:35 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:40 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:45 | runtimeEstimateMinutes | 33.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:50 | runtimeEstimateMinutes | 32.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 09:55 | runtimeEstimateMinutes | 31.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:00 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:05 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:10 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:15 | runtimeEstimateMinutes | 31.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:20 | runtimeEstimateMinutes | 32.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:25 | runtimeEstimateMinutes | 33.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:30 | runtimeEstimateMinutes | 33.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:35 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:40 | runtimeEstimateMinutes | 33.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:45 | runtimeEstimateMinutes | 32.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:50 | runtimeEstimateMinutes | 31.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 10:55 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:00 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:05 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:10 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:15 | runtimeEstimateMinutes | 31.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:20 | runtimeEstimateMinutes | 32.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:25 | runtimeEstimateMinutes | 33.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:30 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:35 | runtimeEstimateMinutes | 33.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:40 | runtimeEstimateMinutes | 32.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:45 | runtimeEstimateMinutes | 31.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:50 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 11:55 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:00 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:05 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:10 | runtimeEstimateMinutes | 31.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:15 | runtimeEstimateMinutes | 32.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:20 | runtimeEstimateMinutes | 33.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:25 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:30 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:35 | runtimeEstimateMinutes | 33.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:40 | runtimeEstimateMinutes | 32.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:45 | runtimeEstimateMinutes | 31.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:50 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 12:55 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:00 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:05 | runtimeEstimateMinutes | 31.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:10 | runtimeEstimateMinutes | 32.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:15 | runtimeEstimateMinutes | 33.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:20 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:25 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:30 | runtimeEstimateMinutes | 33.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:35 | runtimeEstimateMinutes | 32.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:40 | runtimeEstimateMinutes | 31.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:45 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:50 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 13:55 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:00 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:05 | runtimeEstimateMinutes | 31.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:10 | runtimeEstimateMinutes | 32.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:15 | runtimeEstimateMinutes | 33.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:20 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:25 | runtimeEstimateMinutes | 33.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:30 | runtimeEstimateMinutes | 32.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:35 | runtimeEstimateMinutes | 31.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:40 | runtimeEstimateMinutes | 30.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:45 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:50 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 14:55 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:00 | runtimeEstimateMinutes | 31.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:05 | runtimeEstimateMinutes | 32.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:10 | runtimeEstimateMinutes | 33.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:15 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:20 | runtimeEstimateMinutes | 33.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:25 | runtimeEstimateMinutes | 33.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:30 | runtimeEstimateMinutes | 32.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:35 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:40 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:45 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:50 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 15:55 | runtimeEstimateMinutes | 31.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:00 | runtimeEstimateMinutes | 32.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:05 | runtimeEstimateMinutes | 33.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:10 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:15 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:20 | runtimeEstimateMinutes | 33.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:25 | runtimeEstimateMinutes | 32.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:30 | runtimeEstimateMinutes | 31.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:35 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:40 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:45 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:50 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 16:55 | runtimeEstimateMinutes | 32 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:00 | runtimeEstimateMinutes | 33 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:05 | runtimeEstimateMinutes | 33.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:10 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:15 | runtimeEstimateMinutes | 33.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:20 | runtimeEstimateMinutes | 32.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:25 | runtimeEstimateMinutes | 31.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:30 | runtimeEstimateMinutes | 30.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:35 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:40 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:45 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:50 | runtimeEstimateMinutes | 31.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 17:55 | runtimeEstimateMinutes | 32.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:00 | runtimeEstimateMinutes | 33.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:05 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:10 | runtimeEstimateMinutes | 33.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:15 | runtimeEstimateMinutes | 33.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:20 | runtimeEstimateMinutes | 32 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:25 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:30 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:35 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:40 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:45 | runtimeEstimateMinutes | 31.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:50 | runtimeEstimateMinutes | 32.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 18:55 | runtimeEstimateMinutes | 33.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:00 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:05 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:10 | runtimeEstimateMinutes | 33.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:15 | runtimeEstimateMinutes | 32.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:20 | runtimeEstimateMinutes | 31.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:25 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:30 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:35 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:40 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:45 | runtimeEstimateMinutes | 32 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:50 | runtimeEstimateMinutes | 33.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 19:55 | runtimeEstimateMinutes | 33.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:00 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:05 | runtimeEstimateMinutes | 33.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:10 | runtimeEstimateMinutes | 32.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:15 | runtimeEstimateMinutes | 31.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:20 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:25 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:30 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:35 | runtimeEstimateMinutes | 30.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:40 | runtimeEstimateMinutes | 31.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:45 | runtimeEstimateMinutes | 32.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:50 | runtimeEstimateMinutes | 33.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 20:55 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:00 | runtimeEstimateMinutes | 33.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:05 | runtimeEstimateMinutes | 33 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:10 | runtimeEstimateMinutes | 31.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:15 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:20 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:25 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:30 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:35 | runtimeEstimateMinutes | 31.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:40 | runtimeEstimateMinutes | 32.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:45 | runtimeEstimateMinutes | 33.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:50 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 21:55 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:00 | runtimeEstimateMinutes | 33.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:05 | runtimeEstimateMinutes | 32.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:10 | runtimeEstimateMinutes | 31.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:15 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:20 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:25 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:30 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:35 | runtimeEstimateMinutes | 32.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:40 | runtimeEstimateMinutes | 33.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:45 | runtimeEstimateMinutes | 33.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:50 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 22:55 | runtimeEstimateMinutes | 33.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:00 | runtimeEstimateMinutes | 32.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:05 | runtimeEstimateMinutes | 31.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:10 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:15 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:20 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:25 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:30 | runtimeEstimateMinutes | 31.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:35 | runtimeEstimateMinutes | 32.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:40 | runtimeEstimateMinutes | 33.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:45 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:50 | runtimeEstimateMinutes | 33.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 23:55 | runtimeEstimateMinutes | 32.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 | runtimeEstimateMinutes | 31.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 00:05 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 00:10 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 00:15 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 00:20 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 00:25 | runtimeEstimateMinutes | 31.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 00:30 | runtimeEstimateMinutes | 32.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 00:35 | runtimeEstimateMinutes | 33.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 00:40 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 00:45 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 00:50 | runtimeEstimateMinutes | 33.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 00:55 | runtimeEstimateMinutes | 32.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:00 | runtimeEstimateMinutes | 31.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:05 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:10 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:15 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:20 | runtimeEstimateMinutes | 31.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:25 | runtimeEstimateMinutes | 32.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:30 | runtimeEstimateMinutes | 33.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:35 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:40 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:45 | runtimeEstimateMinutes | 33.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:50 | runtimeEstimateMinutes | 32.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 01:55 | runtimeEstimateMinutes | 31.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:00 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:05 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:10 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:15 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:20 | runtimeEstimateMinutes | 31.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:25 | runtimeEstimateMinutes | 32.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:30 | runtimeEstimateMinutes | 33.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:35 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:40 | runtimeEstimateMinutes | 33.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:45 | runtimeEstimateMinutes | 32.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:50 | runtimeEstimateMinutes | 31.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 02:55 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:00 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:05 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:10 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:15 | runtimeEstimateMinutes | 31.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:20 | runtimeEstimateMinutes | 32.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:25 | runtimeEstimateMinutes | 33.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:30 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:35 | runtimeEstimateMinutes | 33.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:40 | runtimeEstimateMinutes | 33.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:45 | runtimeEstimateMinutes | 32.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:50 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 03:55 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:00 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:05 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:10 | runtimeEstimateMinutes | 31.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:15 | runtimeEstimateMinutes | 32.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:20 | runtimeEstimateMinutes | 33.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:25 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:30 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:35 | runtimeEstimateMinutes | 33.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:40 | runtimeEstimateMinutes | 32.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:45 | runtimeEstimateMinutes | 31.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:50 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 04:55 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:00 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:05 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:10 | runtimeEstimateMinutes | 31.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:15 | runtimeEstimateMinutes | 33 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:20 | runtimeEstimateMinutes | 33.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:25 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:30 | runtimeEstimateMinutes | 33.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:35 | runtimeEstimateMinutes | 32.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:40 | runtimeEstimateMinutes | 31.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:45 | runtimeEstimateMinutes | 30.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:50 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 05:55 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:00 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:05 | runtimeEstimateMinutes | 31.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:10 | runtimeEstimateMinutes | 32.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:15 | runtimeEstimateMinutes | 33.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:20 | runtimeEstimateMinutes | 34 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:25 | runtimeEstimateMinutes | 33.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:30 | runtimeEstimateMinutes | 33.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:35 | runtimeEstimateMinutes | 32 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:40 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:45 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:50 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 06:55 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:00 | runtimeEstimateMinutes | 31.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:05 | runtimeEstimateMinutes | 32.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:10 | runtimeEstimateMinutes | 33.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:15 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:20 | runtimeEstimateMinutes | 33.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:25 | runtimeEstimateMinutes | 33.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:30 | runtimeEstimateMinutes | 32.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:35 | runtimeEstimateMinutes | 31.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:40 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:45 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:50 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-14 07:55 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:runtimeEstimateMinutes
UPS-01 | 2026-09-13 08:00 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:05 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:10 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:15 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:20 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:25 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:30 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:35 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:40 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:45 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:50 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:55 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:00 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:05 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:10 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:15 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:20 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:25 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:30 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:35 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:40 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:45 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:50 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 09:55 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:00 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:05 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:10 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:15 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:20 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:25 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:30 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:35 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:40 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:45 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:50 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 10:55 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:00 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:05 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:10 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:15 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:20 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:25 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:30 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:35 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:40 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:45 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:50 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 11:55 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:00 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:05 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:10 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:15 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:20 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:25 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:30 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:35 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:40 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:45 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:50 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 12:55 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:00 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:05 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:10 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:15 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:20 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:25 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:30 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:35 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:40 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:45 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:50 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 13:55 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:00 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:05 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:10 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:15 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:20 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:25 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:30 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:35 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:40 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:45 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:50 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 14:55 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:00 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:05 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:10 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:15 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:20 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:25 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:30 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:35 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:40 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:45 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:50 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 15:55 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:00 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:05 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:10 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:15 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:20 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:25 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:30 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:35 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:40 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:45 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:50 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 16:55 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:00 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:05 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:10 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:15 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:20 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:25 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:30 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:35 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:40 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:45 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:50 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 17:55 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:00 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:05 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:10 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:15 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:20 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:25 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:30 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:35 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:40 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:45 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:50 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 18:55 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:00 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:05 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:10 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:15 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:20 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:25 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:30 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:35 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:40 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:45 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:50 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 19:55 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:00 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:05 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:10 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:15 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:20 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:25 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:30 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:35 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:40 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:45 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:50 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 20:55 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:00 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:05 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:10 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:15 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:20 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:25 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:30 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:35 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:40 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:45 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:50 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 21:55 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:00 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:05 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:10 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:15 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:20 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:25 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:30 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:35 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:40 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:45 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:50 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 22:55 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:00 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:05 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:10 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:15 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:20 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:25 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:30 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:35 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:40 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:45 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:50 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 23:55 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 00:05 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 00:10 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 00:15 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 00:20 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 00:25 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 00:30 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 00:35 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 00:40 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 00:45 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 00:50 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 00:55 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:00 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:05 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:10 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:15 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:20 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:25 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:30 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:35 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:40 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:45 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:50 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 01:55 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:00 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:05 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:10 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:15 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:20 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:25 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:30 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:35 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:40 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:45 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:50 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 02:55 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:00 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:05 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:10 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:15 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:20 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:25 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:30 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:35 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:40 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:45 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:50 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 03:55 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:00 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:05 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:10 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:15 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:20 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:25 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:30 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:35 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:40 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:45 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:50 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 04:55 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:00 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:05 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:10 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:15 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:20 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:25 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:30 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:35 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:40 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:45 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:50 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 05:55 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:00 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:05 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:10 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:15 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:20 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:25 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:30 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:35 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:40 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:45 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:50 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 06:55 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:00 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:05 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:10 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:15 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:20 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:25 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:30 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:35 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:40 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:45 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:50 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-14 07:55 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoc
UPS-01 | 2026-09-13 08:00 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 08:05 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 08:10 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 08:15 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 08:20 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 08:25 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 08:30 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 08:35 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 08:40 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 08:45 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 08:50 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 08:55 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:00 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:05 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:10 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:15 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:20 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:25 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:30 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:35 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:40 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:45 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:50 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 09:55 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:00 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:05 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:10 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:15 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:20 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:25 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:30 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:35 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:40 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:45 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:50 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 10:55 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:00 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:05 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:10 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:15 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:20 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:25 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:30 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:35 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:40 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:45 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:50 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 11:55 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:00 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:05 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:10 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:15 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:20 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:25 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:30 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:35 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:40 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:45 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:50 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 12:55 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:00 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:05 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:10 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:15 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:20 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:25 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:30 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:35 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:40 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:45 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:50 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 13:55 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:00 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:05 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:10 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:15 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:20 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:25 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:30 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:35 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:40 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:45 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:50 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 14:55 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:00 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:05 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:10 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:15 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:20 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:25 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:30 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:35 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:40 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:45 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:50 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 15:55 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:00 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:05 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:10 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:15 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:20 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:25 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:30 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:35 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:40 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:45 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:50 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 16:55 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:00 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:05 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:10 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:15 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:20 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:25 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:30 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:35 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:40 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:45 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:50 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 17:55 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:00 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:05 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:10 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:15 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:20 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:25 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:30 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:35 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:40 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:45 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:50 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 18:55 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:00 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:05 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:10 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:15 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:20 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:25 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:30 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:35 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:40 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:45 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:50 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 19:55 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:00 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:05 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:10 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:15 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:20 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:25 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:30 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:35 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:40 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:45 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:50 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 20:55 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:00 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:05 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:10 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:15 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:20 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:25 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:30 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:35 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:40 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:45 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:50 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 21:55 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:00 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:05 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:10 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:15 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:20 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:25 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:30 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:35 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:40 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:45 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:50 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 22:55 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:00 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:05 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:10 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:15 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:20 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:25 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:30 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:35 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:40 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:45 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:50 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-13 23:55 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 00:05 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 00:10 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 00:15 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 00:20 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 00:25 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 00:30 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 00:35 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 00:40 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 00:45 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 00:50 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 00:55 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:00 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:05 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:10 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:15 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:20 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:25 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:30 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:35 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:40 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:45 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:50 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 01:55 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:00 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:05 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:10 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:15 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:20 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:25 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:30 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:35 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:40 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:45 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:50 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 02:55 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:00 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:05 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:10 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:15 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:20 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:25 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:30 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:35 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:40 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:45 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:50 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 03:55 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:00 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:05 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:10 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:15 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:20 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:25 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:30 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:35 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:40 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:45 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:50 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 04:55 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:00 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:05 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:10 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:15 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:20 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:25 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:30 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:35 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:40 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:45 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:50 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 05:55 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:00 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:05 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:10 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:15 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:20 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:25 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:30 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:35 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:40 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:45 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:50 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 06:55 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:00 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:05 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:10 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:15 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:20 | batterySoh | 94.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:25 | batterySoh | 94.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:30 | batterySoh | 94 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:35 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:40 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:45 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:50 | batterySoh | 93.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-01 | 2026-09-14 07:55 | batterySoh | 93.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-1:batterySoh
UPS-02 | 2026-09-13 08:00 | loadPct | 46.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:05 | loadPct | 45.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:10 | loadPct | 46.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:15 | loadPct | 50 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:20 | loadPct | 53.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:25 | loadPct | 55.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:30 | loadPct | 56.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:35 | loadPct | 55.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:40 | loadPct | 53.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:45 | loadPct | 51.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:50 | loadPct | 49 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:55 | loadPct | 46.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:00 | loadPct | 45.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:05 | loadPct | 45.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:10 | loadPct | 48 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:15 | loadPct | 51.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:20 | loadPct | 54.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:25 | loadPct | 56.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:30 | loadPct | 56 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:35 | loadPct | 55.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:40 | loadPct | 52.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:45 | loadPct | 49.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:50 | loadPct | 46.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 09:55 | loadPct | 45.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:00 | loadPct | 46.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:05 | loadPct | 47.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:10 | loadPct | 51.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:15 | loadPct | 53 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:20 | loadPct | 55.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:25 | loadPct | 56.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:30 | loadPct | 54.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:35 | loadPct | 52.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:40 | loadPct | 50.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:45 | loadPct | 47.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:50 | loadPct | 45.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 10:55 | loadPct | 45.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:00 | loadPct | 47 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:05 | loadPct | 50.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:10 | loadPct | 53.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:15 | loadPct | 53.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:20 | loadPct | 56 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:25 | loadPct | 56.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:30 | loadPct | 54 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:35 | loadPct | 50.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:40 | loadPct | 49.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:45 | loadPct | 47.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:50 | loadPct | 46.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 11:55 | loadPct | 47 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:00 | loadPct | 48.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:05 | loadPct | 51 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:10 | loadPct | 54.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:15 | loadPct | 56.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:20 | loadPct | 56.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:25 | loadPct | 54.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:30 | loadPct | 51.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:35 | loadPct | 49.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:40 | loadPct | 46.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:45 | loadPct | 45.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:50 | loadPct | 45.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 12:55 | loadPct | 48.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:00 | loadPct | 50.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:05 | loadPct | 52.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:10 | loadPct | 55.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:15 | loadPct | 55.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:20 | loadPct | 54.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:25 | loadPct | 52.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:30 | loadPct | 50.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:35 | loadPct | 48.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:40 | loadPct | 46.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:45 | loadPct | 45.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:50 | loadPct | 48.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 13:55 | loadPct | 50.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:00 | loadPct | 53.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:05 | loadPct | 54.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:10 | loadPct | 55.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:15 | loadPct | 56.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:20 | loadPct | 53.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:25 | loadPct | 51.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:30 | loadPct | 47.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:35 | loadPct | 46.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:40 | loadPct | 46 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:45 | loadPct | 47.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:50 | loadPct | 49.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 14:55 | loadPct | 52 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:00 | loadPct | 54.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:05 | loadPct | 54.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:10 | loadPct | 56.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:15 | loadPct | 54.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:20 | loadPct | 50.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:25 | loadPct | 50 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:30 | loadPct | 46 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:35 | loadPct | 46.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:40 | loadPct | 46.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:45 | loadPct | 47.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:50 | loadPct | 51.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 15:55 | loadPct | 53.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:00 | loadPct | 54.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:05 | loadPct | 55.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:10 | loadPct | 54.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:15 | loadPct | 51.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:20 | loadPct | 49.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:25 | loadPct | 47.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:30 | loadPct | 45.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:35 | loadPct | 47 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:40 | loadPct | 48 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:45 | loadPct | 49.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:50 | loadPct | 52.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 16:55 | loadPct | 55.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:00 | loadPct | 56 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:05 | loadPct | 54.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:10 | loadPct | 54 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:15 | loadPct | 50.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:20 | loadPct | 48.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:25 | loadPct | 45.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:30 | loadPct | 45.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:35 | loadPct | 47.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:40 | loadPct | 48.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:45 | loadPct | 52 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:50 | loadPct | 54.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 17:55 | loadPct | 55.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:00 | loadPct | 56.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:05 | loadPct | 53.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:10 | loadPct | 51 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:15 | loadPct | 48.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:20 | loadPct | 47.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:25 | loadPct | 46.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:30 | loadPct | 46.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:35 | loadPct | 48.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:40 | loadPct | 51.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:45 | loadPct | 54 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:50 | loadPct | 56.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 18:55 | loadPct | 55.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:00 | loadPct | 54.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:05 | loadPct | 52.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:10 | loadPct | 49.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:15 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:20 | loadPct | 46.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:25 | loadPct | 46.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:30 | loadPct | 48.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:35 | loadPct | 49.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:40 | loadPct | 53.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:45 | loadPct | 54.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:50 | loadPct | 55.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 19:55 | loadPct | 55.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:00 | loadPct | 53.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:05 | loadPct | 50.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:10 | loadPct | 47.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:15 | loadPct | 46.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:20 | loadPct | 45.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:25 | loadPct | 47.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:30 | loadPct | 50.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:35 | loadPct | 52 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:40 | loadPct | 54.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:45 | loadPct | 55.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:50 | loadPct | 55 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 20:55 | loadPct | 54 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:00 | loadPct | 51.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:05 | loadPct | 48.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:10 | loadPct | 46.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:15 | loadPct | 47 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:20 | loadPct | 46.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:25 | loadPct | 49.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:30 | loadPct | 52.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:35 | loadPct | 53.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:40 | loadPct | 55.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:45 | loadPct | 55 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:50 | loadPct | 53.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 21:55 | loadPct | 53 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:00 | loadPct | 49.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:05 | loadPct | 47 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:10 | loadPct | 46.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:15 | loadPct | 45.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:20 | loadPct | 48.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:25 | loadPct | 50.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:30 | loadPct | 54.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:35 | loadPct | 56.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:40 | loadPct | 55.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:45 | loadPct | 55.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:50 | loadPct | 52.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 22:55 | loadPct | 51.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:00 | loadPct | 48.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:05 | loadPct | 45.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:10 | loadPct | 46.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:15 | loadPct | 47.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:20 | loadPct | 50.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:25 | loadPct | 52.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:30 | loadPct | 55.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:35 | loadPct | 56 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:40 | loadPct | 55.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:45 | loadPct | 53.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:50 | loadPct | 51.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 23:55 | loadPct | 47.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 | loadPct | 46.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 00:05 | loadPct | 45.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 00:10 | loadPct | 46.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 00:15 | loadPct | 49.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 00:20 | loadPct | 51.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 00:25 | loadPct | 54.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 00:30 | loadPct | 56 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 00:35 | loadPct | 55.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 00:40 | loadPct | 53.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 00:45 | loadPct | 53 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 00:50 | loadPct | 49.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 00:55 | loadPct | 46.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:00 | loadPct | 46 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:05 | loadPct | 45.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:10 | loadPct | 47.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:15 | loadPct | 50.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:20 | loadPct | 53.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:25 | loadPct | 54.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:30 | loadPct | 55.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:35 | loadPct | 55.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:40 | loadPct | 52.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:45 | loadPct | 49.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:50 | loadPct | 48.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 01:55 | loadPct | 45.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:00 | loadPct | 45.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:05 | loadPct | 47.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:10 | loadPct | 49.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:15 | loadPct | 52.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:20 | loadPct | 55.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:25 | loadPct | 56.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:30 | loadPct | 55.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:35 | loadPct | 53.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:40 | loadPct | 50 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:45 | loadPct | 49.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:50 | loadPct | 47.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 02:55 | loadPct | 47 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:00 | loadPct | 46.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:05 | loadPct | 49 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:10 | loadPct | 51.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:15 | loadPct | 54.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:20 | loadPct | 55.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:25 | loadPct | 56.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:30 | loadPct | 53.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:35 | loadPct | 52 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:40 | loadPct | 49.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:45 | loadPct | 46.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:50 | loadPct | 46 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 03:55 | loadPct | 46.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:00 | loadPct | 47.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:05 | loadPct | 51 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:10 | loadPct | 54.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:15 | loadPct | 54.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:20 | loadPct | 55.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:25 | loadPct | 55 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:30 | loadPct | 52 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:35 | loadPct | 50.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:40 | loadPct | 47.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:45 | loadPct | 45.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:50 | loadPct | 47 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 04:55 | loadPct | 46.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:00 | loadPct | 50.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:05 | loadPct | 52.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:10 | loadPct | 54.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:15 | loadPct | 56.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:20 | loadPct | 54.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:25 | loadPct | 52.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:30 | loadPct | 50.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:35 | loadPct | 48.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:40 | loadPct | 46.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:45 | loadPct | 46 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:50 | loadPct | 46.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 05:55 | loadPct | 50.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:00 | loadPct | 52.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:05 | loadPct | 55.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:10 | loadPct | 55 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:15 | loadPct | 55 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:20 | loadPct | 54.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:25 | loadPct | 50.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:30 | loadPct | 49.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:35 | loadPct | 47 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:40 | loadPct | 46.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:45 | loadPct | 47.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:50 | loadPct | 48.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 06:55 | loadPct | 50.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:00 | loadPct | 53.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:05 | loadPct | 56.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:10 | loadPct | 55.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:15 | loadPct | 54 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:20 | loadPct | 52.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:25 | loadPct | 49 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:30 | loadPct | 47.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:35 | loadPct | 46 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:40 | loadPct | 46 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:45 | loadPct | 47 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:50 | loadPct | 49.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-14 07:55 | loadPct | 53.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:loadPct
UPS-02 | 2026-09-13 08:00 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:05 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:10 | runtimeEstimateMinutes | 27.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:15 | runtimeEstimateMinutes | 28.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:20 | runtimeEstimateMinutes | 29.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:25 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:30 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:35 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:40 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:45 | runtimeEstimateMinutes | 29.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:50 | runtimeEstimateMinutes | 28.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:55 | runtimeEstimateMinutes | 27.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:00 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:05 | runtimeEstimateMinutes | 27.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:10 | runtimeEstimateMinutes | 28.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:15 | runtimeEstimateMinutes | 29.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:20 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:25 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:30 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:35 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:40 | runtimeEstimateMinutes | 29.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:45 | runtimeEstimateMinutes | 28.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:50 | runtimeEstimateMinutes | 27.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 09:55 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:00 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:05 | runtimeEstimateMinutes | 27.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:10 | runtimeEstimateMinutes | 28.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:15 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:20 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:25 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:30 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:35 | runtimeEstimateMinutes | 29.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:40 | runtimeEstimateMinutes | 28.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:45 | runtimeEstimateMinutes | 27.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:50 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 10:55 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:00 | runtimeEstimateMinutes | 27.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:05 | runtimeEstimateMinutes | 28.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:10 | runtimeEstimateMinutes | 29.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:15 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:20 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:25 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:30 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:35 | runtimeEstimateMinutes | 29 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:40 | runtimeEstimateMinutes | 28 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:45 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:50 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 11:55 | runtimeEstimateMinutes | 27.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:00 | runtimeEstimateMinutes | 28.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:05 | runtimeEstimateMinutes | 29.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:10 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:15 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:20 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:25 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:30 | runtimeEstimateMinutes | 29.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:35 | runtimeEstimateMinutes | 28.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:40 | runtimeEstimateMinutes | 27.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:45 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:50 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 12:55 | runtimeEstimateMinutes | 27.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:00 | runtimeEstimateMinutes | 29 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:05 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:10 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:15 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:20 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:25 | runtimeEstimateMinutes | 29.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:30 | runtimeEstimateMinutes | 28.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:35 | runtimeEstimateMinutes | 27.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:40 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:45 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:50 | runtimeEstimateMinutes | 27.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 13:55 | runtimeEstimateMinutes | 28.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:00 | runtimeEstimateMinutes | 29.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:05 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:10 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:15 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:20 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:25 | runtimeEstimateMinutes | 29 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:30 | runtimeEstimateMinutes | 27.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:35 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:40 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:45 | runtimeEstimateMinutes | 27.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:50 | runtimeEstimateMinutes | 28.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 14:55 | runtimeEstimateMinutes | 29.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:00 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:05 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:10 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:15 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:20 | runtimeEstimateMinutes | 29.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:25 | runtimeEstimateMinutes | 28.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:30 | runtimeEstimateMinutes | 27.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:35 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:40 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:45 | runtimeEstimateMinutes | 28 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:50 | runtimeEstimateMinutes | 29.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 15:55 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:00 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:05 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:10 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:15 | runtimeEstimateMinutes | 29.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:20 | runtimeEstimateMinutes | 28.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:25 | runtimeEstimateMinutes | 27.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:30 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:35 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:40 | runtimeEstimateMinutes | 27.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:45 | runtimeEstimateMinutes | 28.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:50 | runtimeEstimateMinutes | 29.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 16:55 | runtimeEstimateMinutes | 30.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:00 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:05 | runtimeEstimateMinutes | 30.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:10 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:15 | runtimeEstimateMinutes | 28.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:20 | runtimeEstimateMinutes | 27.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:25 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:30 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:35 | runtimeEstimateMinutes | 27.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:40 | runtimeEstimateMinutes | 28.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:45 | runtimeEstimateMinutes | 29.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:50 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 17:55 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:00 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:05 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:10 | runtimeEstimateMinutes | 29.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:15 | runtimeEstimateMinutes | 28.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:20 | runtimeEstimateMinutes | 27.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:25 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:30 | runtimeEstimateMinutes | 27.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:35 | runtimeEstimateMinutes | 28.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:40 | runtimeEstimateMinutes | 29.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:45 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:50 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 18:55 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:00 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:05 | runtimeEstimateMinutes | 29.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:10 | runtimeEstimateMinutes | 28.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:15 | runtimeEstimateMinutes | 27.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:20 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:25 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:30 | runtimeEstimateMinutes | 27.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:35 | runtimeEstimateMinutes | 28.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:40 | runtimeEstimateMinutes | 29.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:45 | runtimeEstimateMinutes | 30.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:50 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 19:55 | runtimeEstimateMinutes | 30.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:00 | runtimeEstimateMinutes | 29.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:05 | runtimeEstimateMinutes | 28.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:10 | runtimeEstimateMinutes | 27.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:15 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:20 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:25 | runtimeEstimateMinutes | 27.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:30 | runtimeEstimateMinutes | 28.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:35 | runtimeEstimateMinutes | 29.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:40 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:45 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:50 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 20:55 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:00 | runtimeEstimateMinutes | 29.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:05 | runtimeEstimateMinutes | 28.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:10 | runtimeEstimateMinutes | 27.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:15 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:20 | runtimeEstimateMinutes | 27.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:25 | runtimeEstimateMinutes | 28.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:30 | runtimeEstimateMinutes | 29.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:35 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:40 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:45 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:50 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 21:55 | runtimeEstimateMinutes | 29.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:00 | runtimeEstimateMinutes | 28.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:05 | runtimeEstimateMinutes | 27.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:10 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:15 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:20 | runtimeEstimateMinutes | 27.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:25 | runtimeEstimateMinutes | 28.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:30 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:35 | runtimeEstimateMinutes | 30.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:40 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:45 | runtimeEstimateMinutes | 30.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:50 | runtimeEstimateMinutes | 29.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 22:55 | runtimeEstimateMinutes | 28.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:00 | runtimeEstimateMinutes | 27.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:05 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:10 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:15 | runtimeEstimateMinutes | 27.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:20 | runtimeEstimateMinutes | 28.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:25 | runtimeEstimateMinutes | 29.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:30 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:35 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:40 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:45 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:50 | runtimeEstimateMinutes | 29.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 23:55 | runtimeEstimateMinutes | 28 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 00:05 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 00:10 | runtimeEstimateMinutes | 27.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 00:15 | runtimeEstimateMinutes | 28.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 00:20 | runtimeEstimateMinutes | 29.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 00:25 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 00:30 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 00:35 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 00:40 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 00:45 | runtimeEstimateMinutes | 29.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 00:50 | runtimeEstimateMinutes | 28.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 00:55 | runtimeEstimateMinutes | 27.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:00 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:05 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:10 | runtimeEstimateMinutes | 27.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:15 | runtimeEstimateMinutes | 29 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:20 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:25 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:30 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:35 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:40 | runtimeEstimateMinutes | 29.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:45 | runtimeEstimateMinutes | 28.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:50 | runtimeEstimateMinutes | 27.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 01:55 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:00 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:05 | runtimeEstimateMinutes | 27.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:10 | runtimeEstimateMinutes | 28.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:15 | runtimeEstimateMinutes | 29.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:20 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:25 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:30 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:35 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:40 | runtimeEstimateMinutes | 29 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:45 | runtimeEstimateMinutes | 27.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:50 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 02:55 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:00 | runtimeEstimateMinutes | 27.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:05 | runtimeEstimateMinutes | 28.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:10 | runtimeEstimateMinutes | 29.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:15 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:20 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:25 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:30 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:35 | runtimeEstimateMinutes | 29.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:40 | runtimeEstimateMinutes | 28.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:45 | runtimeEstimateMinutes | 27.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:50 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 03:55 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:00 | runtimeEstimateMinutes | 28 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:05 | runtimeEstimateMinutes | 29 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:10 | runtimeEstimateMinutes | 30.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:15 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:20 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:25 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:30 | runtimeEstimateMinutes | 29.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:35 | runtimeEstimateMinutes | 28.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:40 | runtimeEstimateMinutes | 27.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:45 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:50 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 04:55 | runtimeEstimateMinutes | 27.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:00 | runtimeEstimateMinutes | 28.7 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:05 | runtimeEstimateMinutes | 29.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:10 | runtimeEstimateMinutes | 30.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:15 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:20 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:25 | runtimeEstimateMinutes | 30 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:30 | runtimeEstimateMinutes | 28.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:35 | runtimeEstimateMinutes | 27.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:40 | runtimeEstimateMinutes | 27.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:45 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:50 | runtimeEstimateMinutes | 27.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 05:55 | runtimeEstimateMinutes | 28.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:00 | runtimeEstimateMinutes | 29.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:05 | runtimeEstimateMinutes | 30.4 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:10 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:15 | runtimeEstimateMinutes | 30.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:20 | runtimeEstimateMinutes | 30.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:25 | runtimeEstimateMinutes | 29.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:30 | runtimeEstimateMinutes | 28.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:35 | runtimeEstimateMinutes | 27.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:40 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:45 | runtimeEstimateMinutes | 27.3 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:50 | runtimeEstimateMinutes | 28.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 06:55 | runtimeEstimateMinutes | 29.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:00 | runtimeEstimateMinutes | 30.2 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:05 | runtimeEstimateMinutes | 30.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:10 | runtimeEstimateMinutes | 31 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:15 | runtimeEstimateMinutes | 30.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:20 | runtimeEstimateMinutes | 29.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:25 | runtimeEstimateMinutes | 28.5 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:30 | runtimeEstimateMinutes | 27.6 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:35 | runtimeEstimateMinutes | 27 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:40 | runtimeEstimateMinutes | 27.1 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:45 | runtimeEstimateMinutes | 27.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:50 | runtimeEstimateMinutes | 28.8 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-14 07:55 | runtimeEstimateMinutes | 29.9 | min | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:runtimeEstimateMinutes
UPS-02 | 2026-09-13 08:00 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:05 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:10 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:15 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:20 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:25 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:30 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:35 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:40 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:45 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:50 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:55 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:00 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:05 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:10 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:15 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:20 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:25 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:30 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:35 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:40 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:45 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:50 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 09:55 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:00 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:05 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:10 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:15 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:20 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:25 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:30 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:35 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:40 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:45 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:50 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 10:55 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:00 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:05 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:10 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:15 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:20 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:25 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:30 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:35 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:40 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:45 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:50 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 11:55 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:00 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:05 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:10 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:15 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:20 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:25 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:30 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:35 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:40 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:45 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:50 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 12:55 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:00 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:05 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:10 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:15 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:20 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:25 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:30 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:35 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:40 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:45 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:50 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 13:55 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:00 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:05 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:10 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:15 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:20 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:25 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:30 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:35 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:40 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:45 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:50 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 14:55 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:00 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:05 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:10 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:15 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:20 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:25 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:30 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:35 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:40 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:45 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:50 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 15:55 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:00 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:05 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:10 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:15 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:20 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:25 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:30 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:35 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:40 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:45 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:50 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 16:55 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:00 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:05 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:10 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:15 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:20 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:25 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:30 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:35 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:40 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:45 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:50 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 17:55 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:00 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:05 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:10 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:15 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:20 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:25 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:30 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:35 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:40 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:45 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:50 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 18:55 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:00 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:05 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:10 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:15 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:20 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:25 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:30 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:35 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:40 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:45 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:50 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 19:55 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:00 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:05 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:10 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:15 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:20 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:25 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:30 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:35 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:40 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:45 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:50 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 20:55 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:00 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:05 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:10 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:15 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:20 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:25 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:30 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:35 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:40 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:45 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:50 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 21:55 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:00 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:05 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:10 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:15 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:20 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:25 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:30 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:35 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:40 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:45 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:50 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 22:55 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:00 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:05 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:10 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:15 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:20 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:25 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:30 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:35 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:40 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:45 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:50 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 23:55 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 00:05 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 00:10 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 00:15 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 00:20 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 00:25 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 00:30 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 00:35 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 00:40 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 00:45 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 00:50 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 00:55 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:00 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:05 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:10 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:15 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:20 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:25 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:30 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:35 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:40 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:45 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:50 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 01:55 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:00 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:05 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:10 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:15 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:20 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:25 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:30 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:35 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:40 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:45 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:50 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 02:55 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:00 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:05 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:10 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:15 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:20 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:25 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:30 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:35 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:40 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:45 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:50 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 03:55 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:00 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:05 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:10 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:15 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:20 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:25 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:30 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:35 | batterySoc | 96.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:40 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:45 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:50 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 04:55 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:00 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:05 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:10 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:15 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:20 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:25 | batterySoc | 97.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:30 | batterySoc | 97 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:35 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:40 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:45 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:50 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 05:55 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:00 | batterySoc | 97.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:05 | batterySoc | 97.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:10 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:15 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:20 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:25 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:30 | batterySoc | 96.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:35 | batterySoc | 96.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:40 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:45 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:50 | batterySoc | 96.5 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 06:55 | batterySoc | 97.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:00 | batterySoc | 97.6 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:05 | batterySoc | 97.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:10 | batterySoc | 98 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:15 | batterySoc | 97.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:20 | batterySoc | 97.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:25 | batterySoc | 96.7 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:30 | batterySoc | 96.3 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:35 | batterySoc | 96 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:40 | batterySoc | 96.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:45 | batterySoc | 96.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:50 | batterySoc | 96.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-14 07:55 | batterySoc | 97.4 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoc
UPS-02 | 2026-09-13 08:00 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 08:05 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 08:10 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 08:15 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 08:20 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 08:25 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 08:30 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 08:35 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 08:40 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 08:45 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 08:50 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 08:55 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:00 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:05 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:10 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:15 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:20 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:25 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:30 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:35 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:40 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:45 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:50 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 09:55 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:00 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:05 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:10 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:15 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:20 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:25 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:30 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:35 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:40 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:45 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:50 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 10:55 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:00 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:05 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:10 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:15 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:20 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:25 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:30 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:35 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:40 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:45 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:50 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 11:55 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:00 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:05 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:10 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:15 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:20 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:25 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:30 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:35 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:40 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:45 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:50 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 12:55 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:00 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:05 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:10 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:15 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:20 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:25 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:30 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:35 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:40 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:45 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:50 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 13:55 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:00 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:05 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:10 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:15 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:20 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:25 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:30 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:35 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:40 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:45 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:50 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 14:55 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:00 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:05 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:10 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:15 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:20 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:25 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:30 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:35 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:40 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:45 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:50 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 15:55 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:00 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:05 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:10 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:15 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:20 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:25 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:30 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:35 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:40 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:45 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:50 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 16:55 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:00 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:05 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:10 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:15 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:20 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:25 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:30 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:35 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:40 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:45 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:50 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 17:55 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:00 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:05 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:10 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:15 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:20 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:25 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:30 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:35 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:40 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:45 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:50 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 18:55 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:00 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:05 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:10 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:15 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:20 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:25 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:30 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:35 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:40 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:45 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:50 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 19:55 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:00 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:05 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:10 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:15 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:20 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:25 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:30 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:35 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:40 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:45 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:50 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 20:55 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:00 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:05 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:10 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:15 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:20 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:25 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:30 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:35 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:40 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:45 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:50 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 21:55 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:00 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:05 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:10 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:15 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:20 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:25 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:30 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:35 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:40 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:45 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:50 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 22:55 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:00 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:05 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:10 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:15 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:20 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:25 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:30 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:35 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:40 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:45 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:50 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-13 23:55 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 00:05 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 00:10 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 00:15 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 00:20 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 00:25 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 00:30 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 00:35 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 00:40 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 00:45 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 00:50 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 00:55 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:00 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:05 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:10 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:15 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:20 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:25 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:30 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:35 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:40 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:45 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:50 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 01:55 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:00 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:05 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:10 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:15 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:20 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:25 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:30 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:35 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:40 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:45 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:50 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 02:55 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:00 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:05 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:10 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:15 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:20 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:25 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:30 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:35 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:40 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:45 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:50 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 03:55 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:00 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:05 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:10 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:15 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:20 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:25 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:30 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:35 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:40 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:45 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:50 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 04:55 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:00 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:05 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:10 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:15 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:20 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:25 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:30 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:35 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:40 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:45 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:50 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 05:55 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:00 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:05 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:10 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:15 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:20 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:25 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:30 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:35 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:40 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:45 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:50 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 06:55 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:00 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:05 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:10 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:15 | batterySoh | 92.2 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:20 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:25 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:30 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:35 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:40 | batterySoh | 91.8 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:45 | batterySoh | 91.9 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:50 | batterySoh | 92 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh
UPS-02 | 2026-09-14 07:55 | batterySoh | 92.1 | % | good |  | sim-mapping-1 | Simulated Data | complete/1.0 | sim:session-1:g3:ups-2:batterySoh

## Alarms & Events
Equipment | Category | Occurrence ID | Severity | Description | Occurred At | Cleared At | Acknowledgment | Acknowledged At | Period Classification | Duration in Range (Seconds) | Rule | Source
UPS-01 | event | sim:session-1:g3:plan-0 | info | UPS-01 Scheduled Maintenance Reminder (Simulated) | 2026-09-14 07:00 | Event | notRequired |  | New Occurrence | 3600 | R-04 | Simulated Data
UPS-01 | alarm | sim:session-1:g3:restored-0 | warning | UPS-01 Historical Utility Outage (Simulated) | 2026-09-14 06:00 | 2026-09-14 06:01 | acknowledged | 2026-09-14 06:01 | New Occurrence | 60 | native-sim | Simulated Data
UPS-02 | event | sim:session-1:g3:plan-1 | info | UPS-02 Scheduled Maintenance Reminder (Simulated) | 2026-09-14 07:00 | Event | notRequired |  | New Occurrence | 3600 | R-04 | Simulated Data
UPS-02 | alarm | sim:session-1:g3:restored-1 | warning | UPS-02 Historical Utility Outage (Simulated) | 2026-09-14 06:00 | 2026-09-14 06:01 | acknowledged | 2026-09-14 06:01 | New Occurrence | 60 | native-sim | Simulated Data
UPS-01 | alarm | sim:session-1:g3:past-alarm | warning | Historical Boundary Test (Simulated) | 2026-09-14 07:00 | Ongoing | unacknowledged |  | New Occurrence | 3600 | R-02 | Simulated Data