## Notes
UPS Fleet Monitor | Maintenance & Health · Current Assessment · Simulated Data
Historical Boundary | State immediately before the cutoff; later acknowledgments/recoveries are excluded
Source | Simulated Data / simulation
Session | session-1
Generation | g3
Seed | 7
Current Scenario Version | missing/1.0; historical rows identify their source scenario
Template / Dictionary | REP-04 / 1.0
Start (Inclusive) | 2026-09-13 08:00
End (Exclusive) | 2026-09-14 08:00
Time Zone | Asia/Singapore
Data Cutoff | 2026-09-14 08:00
Generated At | 2026-09-14T16:52:03.818Z
Statistical Method | Valid-time weighting; gaps are not filled with zero; source peaks; simulated assessments are not certified
Completeness | Full coverage for the selected metrics

## Metric Dictionary
ID | Name | Definition | Unit | Location | Basis | Formula | Threshold
KPI-01 | Power Mode | The equipment's operating mode, independent of communication status. | Status | UPS | Vendor Protocol Enumeration | Not Calculated | No universal numeric threshold; display the mapped state.
KPI-02 | Equipment Identity | Name, model, location, and selected asset identity. This is not a performance score. | — | Asset Register | Vendor Model and Engineering Asset Register | Not Calculated | No Performance Threshold
KPI-03 | Estimated Runtime R | Remaining supply time estimated by the equipment at the current load. This is not a guaranteed duration. | min | UPS | Equipment Runtime Algorithm | Estimated by the equipment; not inferred linearly from voltage. | Triggered when R < Q. Q is a project requirement, not a universal industry limit.
KPI-04 | Required Runtime Q and Margin | Q comes from project business requirements. Margin is estimated runtime minus required runtime. | min | UPS / Project Requirement | Project Continuity Requirement | M = R − Q, calculated only when R is valid. | Q, recovery hysteresis, and valid-sample gates follow the approved configuration.
KPI-05 | Overall Health Score | An independent vendor or approved external assessment. Do not combine SOC, SOH, or alarm counts into a score. | 0–100 points | UPS | Approved External Overall Health Method | This project defines no universal overall health formula. | Without a valid score, show a neutral unassessed ring. A high score does not override critical risk.
KPI-06 | Battery Asset | Chemistry, cell count, and identity of the selected battery string. | cells | Selected Battery String | Vendor Battery Register | Not Calculated | Different battery chemistries must not share an assumed default threshold.
KPI-07 | Battery String Voltage | Voltage across the selected string terminals, distinct from individual cell voltage. | V | Battery String Terminals | Model Point List, Scaling, and Measurement Location | Raw value × approved scale + offset | Vendor operating limits are pending; no universal limit is assumed.
KPI-08 | Impedance and Baseline | A result from a specified measurement method. DC resistance and AC impedance are not interchangeable. | mΩ / % | Selected Battery String | Baseline Using the Same Instrument, Method, Temperature, and Charge State | Change = (current − baseline) / baseline × 100%; baseline > 0 | R-03 requires vendor thresholds or an approved baseline.
KPI-09 | Battery Temperature | Temperature at the battery sensor location. | °C / °F | Selected Battery String | Vendor Temperature Sensor Definition | °F=°C×1.8+32 | Vendor temperature limits are pending. No cross-chemistry default is used.
KPI-10 | Charge / Discharge Current | Charging or bidirectional battery current with its sign convention preserved. | A | Battery String Circuit | Measurement Direction in the Point List | Normalize raw current; a negative sign alone does not indicate a fault. | The sign convention follows the source point mapping.
KPI-11 | SOC and SOH | SOC indicates remaining charge. SOH is capacity-based or vendor-defined health; they are independent. | % | Selected Battery String | Vendor Capacity-Based SOH Definition | Capacity SOH = measured capacity / reference rated capacity × 100% under matching conditions. SOC uses the vendor full-charge reference. | No universal retirement threshold across chemistries.
KPI-12 | Battery History | Explicit SOC or SOH history with a time axis, units, and quality gaps. | % | Selected Battery String | FIN History | Aggregate valid samples; do not fill gaps with zero or connect lines across gaps. | Do not extrapolate service life from the curve.
KPI-13 | Battery Maintenance / Replacement Window | A date range from a maintenance plan, vendor recommendation, or traceable external prediction. | Date Range | Battery Component | Maintenance Plan or External Model | Do not calculate unverified remaining months. | If the source, method, or valid dates are incomplete, show Not Assessed.
KPI-14 | Active / Apparent Power and Ratings | Compare kW and kVA with their respective ratings on the same basis. Do not divide one by the other for load percentage. | kW / kVA | UPS Output / Nameplate | Model Ratings and Derating Conditions | Power is measured; ratings are asset configuration values. | Rated capacity is stored per equipment item.
KPI-15 | Load Percentage | Power as a percentage of rated capacity on the same basis. Use a distinct name for a different native definition. | % | UPS Output | Vendor Load Definition and Project Rules | P / rated P × 100% or S / rated S × 100%; use the declared mapping basis. | Thresholds, hysteresis, and gates follow approved project rules. Preserve values above 100%.
KPI-16 | Load History | Time series using the declared load basis. | % | UPS | Source Sample History | Weighted by Valid Time | Do not fill gaps with zero. Report coverage and source peaks separately.
KPI-17 | Output Voltage and Frequency | Identify the output or internal inverter location, phase, and line-to-line or phase voltage basis. | V / Hz | L1-N / UPS Output | Vendor Performance Declaration; IEC 62040-3 Provides Background Only | Direct Measurement | Specific tolerances await equipment and project design. No standards conformity is certified.
KPI-18 | Output THD | Distinguish THDv from THDi and THD-F from THD-R. | % | Output L1 / Voltage | Vendor THD-F Measurement Window | THD-F=√Σ(Xn²,n≥2)/X1×100% | Slow history cannot reconstruct harmonics. Vendor limits must be registered.
KPI-19 | Rectifier / Charger | Rectifier operation and charging operation are separate states. | Status | Power Module | Vendor Enums and Operating States | Not Calculated | Unknown must not be displayed as Normal.
KPI-20 | Cooling Fan | Actual fan feedback, not a remaining-life percentage. | Status | Selected Power Module | Vendor Fan Diagnostic Enumeration | Not Calculated | Do not display remaining life without evidence.
KPI-21 | Capacitor Health | A vendor or external assessment percentage, not a universal direct measurement. | % | Capacitor Bank | Vendor Capacitor Assessment Method | Use a traceable external assessment, not an invented algorithm. | Without a source, leave the track empty. Do not fill it to 100%.
KPI-22 | Ambient Temperature | Room or cabinet sensor temperature, distinct from battery temperature. | °C / °F | Associated Space / Environmental Sensor | Sensor Location and Vendor Operating Conditions | °F=°C×1.8+32 | 20–25°C is not an automatically enforced project standard.
KPI-23 | Relative Humidity | Relative humidity in the specified space. Retain out-of-range observations but exclude them from assessment. | %RH | Associated Space | Vendor Sensor Range | Not Calculated | Out-of-range observations are not valid inputs.
KPI-24 | Air Quality | Specify the pollutant, unit, or defined classification system. | μg/m³ / Class | Associated Space Sensor | PM2.5 and Vendor Classification | Use the Sensor Definition | Do not label an arbitrary index as a standardized AQI.
KPI-25 | Water Detection | Three states: Dry, Water Detected, and Unknown. | Boolean / State | Leak Sensor Area | Vendor Digital Input Enumeration | false = Dry; true = Water Detected; null = Unknown | Unknown does not mean Dry.
KPI-26 | Transfer Status | Actual equipment transfer-switch state. | Status | UPS Transfer Switch | Vendor Switch Enumeration | Not Calculated | Do not infer power mode from communication status.
KPI-27 | Static / Maintenance Bypass | Availability and activation represent capability and present engagement separately. | Boolean / State | Static Bypass / Maintenance Bypass | Vendor UPS and Switch Enums | Independent fields; do not infer one from another. | Available does not mean Active. Keep the state Unknown when disconnected.
KPI-28 | Last Transfer Duration | Transfer duration recorded by the equipment. | ms | Equipment Transfer Event | Trusted Equipment Event | Use measured event duration, not a polling interval. | Without event evidence, show Unsupported.
KPI-29 | Last Transfer Time | The timestamp of the last equipment transfer event, including its time zone. | ISO Timestamp | Equipment Event | Native event record | Not Calculated | Not the page refresh or receipt time
KPI-30 | Maintenance Outlook | Manual plans or external recommendations for batteries, capacitors, and fans. | Date Range | Applicable component | Plan owner, manufacturer recommendation, or existing model | No proprietary prediction is generated | No month estimate without a source; manual plans are clearly identified
KPI-31 | Alarms & Events | FIN occurrence, recovery, and acknowledgment are independent lifecycle events. | Event / Time | Current UPS alarm scope | Native instance and lifecycle | New occurrences and carry-over instances are counted separately | Ordinary events are excluded from alarm counts
KPI-32 | Active / Unacknowledged Count | Active instances and unacknowledged instances in the current scope are counted separately. | items | Current filters and authorized scope | FIN native lifecycle | Deduplicate by instance ID; acknowledgment does not change active state | Acknowledged critical alarms remain critical; counts are unknown when the source is unavailable

## Data Quality
Equipment | Metric | Valid Samples | Total Samples | Coverage % | Valid Mean | Source Minimum | Source Maximum
UPS-01 | loadPct | 288 | 288 | 100 | 43.918 | 38 | 49.8
UPS-01 | runtimeEstimateMinutes | 288 | 288 | 100 | 31.976 | 30 | 34
UPS-01 | batterySoc | 288 | 288 | 100 | 96.987 | 96 | 98
UPS-01 | batterySoh | 288 | 288 | 100 | 93.998 | 93.8 | 94.2
UPS-02 | loadPct | 288 | 288 | 100 | 50.89 | 45.2 | 56.9
UPS-02 | runtimeEstimateMinutes | 288 | 288 | 100 | 28.984 | 27 | 31
UPS-02 | batterySoc | 288 | 288 | 100 | 96.991 | 96 | 98
UPS-02 | batterySoh | 288 | 288 | 100 | 91.997 | 91.8 | 92.2

## Maintenance Health
Equipment | Component | Category | Notes | Start / Due | End | Basis | Assessed At | Source
UPS-01 | battery | planned | Battery Capacity Review (Simulated Plan) | 2026-12-13 |  | sim-plan-v1 | 2026-09-14 08:03 | Simulated Data
UPS-01 | capacitor | externalPrediction | Simulated Assessment Window · Not Vendor Validated | 2027-02-11 | 2027-04-12 | sim-assessment-v1 | 2026-09-14 08:03 | Simulated Data
UPS-01 | fan | planned | Fan Cleaning and Speed Check (Simulated Plan) | 2026-10-14 |  | sim-plan-v1 | 2026-09-14 08:03 | Simulated Data
UPS-02 | battery | planned | Battery Capacity Review (Simulated Plan) | 2026-12-13 |  | sim-plan-v1 | 2026-09-14 08:03 | Simulated Data
UPS-02 | capacitor | externalPrediction | Simulated Assessment Window · Not Vendor Validated | 2027-02-11 | 2027-04-12 | sim-assessment-v1 | 2026-09-14 08:03 | Simulated Data
UPS-02 | fan | planned | Fan Cleaning and Speed Check (Simulated Plan) | 2026-10-14 |  | sim-plan-v1 | 2026-09-14 08:03 | Simulated Data

## Current Health
Equipment | SOC% | SOH% | Simulated Health Score | Risk | Coverage | Assessed At | Basis | Source | Active Alarms | Unacknowledged
UPS-01 |  |  |  | attention | partial | 2026-09-14 08:03 | sim-assessment-v1 | Simulated Data | 2 | 1
UPS-02 |  |  |  | attention | partial | 2026-09-14 08:03 | sim-assessment-v1 | Simulated Data | 1 | 1